## Electrical BOQ
Sr. No | Descriptions | Qty | Unit | Supply |  | Installation |  | Total Amount
|  |  |  | Rate | Amount | Rate | Amount
A | MAIN AND SUB - PANELS
1 | Supply, Installation, testing and commissioning of PCC, Main and Sub Panels as per drawing and specifications. Panel should be dust and vermin proof (IP-52). Panel shall be fabricated from 14 /16 SWG CRCA sheet metal duly painted with seven tank process and poweder coated of approved paints. Panel consisting of following.......
Note : All MCCBs shall be Ics = 100 % Icu and to be adjustables. All MCB shall be 10kA - C-Curve,
1a | MAIN PANEL
- Incomming : 400 A TP MCCB, MPR, 50 KA
- 400 A, 440V, TPN, Cu. Busbars, 50kA / 1 Sec.
- 25 x 6 mm Cu. Earth Busbars
- Load managers with all accessories.
- indicating lamps
Outgoing Feeders :
- 200 A TP MCCB,T/M, 35 kA, (1 no.)
- 125 A TP MCCB,T/M, 35 kA, (1 no.)
- 100 A TP MCCB,T/M, 35 kA, (1 no.)
- 63 A TP MCCB,T/M, 25 kA, (1 no.)
- 40/63 A FP MCB, 10 kA (10 nos.)
| - 16 to 32 A DP MCB, 10 kA (2 nos.) | 1 | nos.
1b | SUB PANEL-1
- Incomming : 200 A TP MCCB, T/M, 35 KA
- 250 A, 440V, TPN, Cu. Busbars,
- 25 x 6 mm Cu. Earth Busbars
- Load managers with all accessories.
- indicating lamps
Outgoing Feeders :
- 63 A TP MCCB,T/M, 25 kA, (2 nos.)
| - 40/63 A FP MCB, 10 kA (12 nos.) | 1 | nos.
1c | SUB PANEL-2
- Incomming : 125 A TP MCCB, T/M, 35 KA
- 200 A, 440V, TPN, Cu. Busbars,
- 25 x 3 mm Cu. Earth Busbars
- Load managers with all accessories.
- indicating lamps
Outgoing Feeders :
- 40/63 A FP MCB, 10 kA (10 nos.)
| - 16 to 32 A DP MCB, 10 kA (2 nos.) | 1 | nos.
TOTAL- A - MAIN AND SUB - PANELS
B | LIGHTING, POWER & COMPUTER POWER SUPPLY DISTRIBUTION BOARDS
2 | Supply, installing, loading, un-loading, shifting from store with testing and commissioning of metallic double door type distribution board with following MCBs / ELMCBs / RCCBs / etc. with all necessary connections, remaining blank area shall be covered with blanking (dummy) plates etc. complete. (All DBs shall be installed concealed)
2a | 4-WAY TPN PPI DB :
Incoming : 40 A FP MCB
Sub Incoming : 32 A DP RCCB - 100 mA (3 nos)
| Outgoing : 6 to 32 A SP MCB (6 nos) | 1 | nos.
2b | 6-WAY TPN PPI DB :
Incoming : 63 / 40 A FP MCB
Sub Incoming : 40 A DP RCCB - 100 mA (3 nos)
| Outgoing : 6 to 32 A SP MCB (12 nos) | 10 | nos.
2c | 8-WAY TPN PPI DB :
Incoming : 63 / 40 A FP MCB
Sub Incoming : 40 A DP RCCB - 100 mA (3 nos)
| Outgoing : 6 to 32 A SP MCB (18 nos) | 12 | nos.
2d | 4-WAY VTPN DB : Suitable for Incommer FP MCB and SP/TP MCBs as outgoings
Incoming : 63 / 40 A FP MCB
Outgoing : 10 to 32 A TP MCBs (4 Nos.)
| : 10 to 25 A SP MCBs (2 nos.) | 1 | nos.
2e | 8 - Way SPN DB :
Incoming : 32 A DP RCBO - 30 mA
| Outgoing : 6 to 20 A SP MCB (4 nos.) | 1 | nos.
TOTAL - B - FOR DISTRIBUTION BOARDS
C | POWER & CONTROL CABLES :
3 | Supply, laying, installation, testing and commissioning of armoured PVC / XLPE insulated alumunium / copper conductor of the following sizes in existing cable trench / pull - through pipes / on cable tray or duly cleated on wall / RCC beam / slab / column / structural steel with GI heavy duty patti spacers and GI saddles with necessary drilling and welding on structural steel etc. including supply and fixing alluminium tag numbers at every two meter etc, complete to the satisfaction of EIC (Verify the actual legnth as per the cable schedule and preparing the drum legnth before procurement)
3a | 3.5 x 120 sq.mm Alu. A2XFY cable | 230 | mts
3b | 3.5 x 70 sq.mm Alu. A2XFY cable | 180 | mts
3c | 4 x 16 sq.mm Alu. A2XFY cable | 600 | mts
3d | 4 x 2.5 sq.mm Cu. YWY cable | 400 | mts
3e | 3 x 2.5 sq.mm Cu. YWY cable | 300 | mts
TOTAL - C - POWER & CONTROL CABLES :
D | END TERMINATIONS
4 | End termination of following PVC / XLPE insulated armoured cables including supply and fixing of brass heavy duty double compression type cable glands with PVC hoods and crimping type long barrel heavy duty copper / alluminum lugs (as per conductor of cable) suitable for terminations of armoured cables, including making connection / terminations of all leads of cables, including drilling and tapping of equipment for cable entries as required and including all labour and materials complete to the satisfaction of E.I.C
4a | 3.5 x 120 sq.mm Alu. A2XFY cable | 6 | nos
4b | 3.5 x 70 sq.mm Alu. A2XFY cable | 2 | nos
4c | 4 x 16 sq.mm Alu. A2XFY cable | 36 | nos
4d | 3 or 4 x 2.5 sq.mm Cu. YWY cable | 80 | nos
TOTAL - D - END TERMINATIONS
E | EARTHING SYSTEM :
5 | Providing and making Earthing Pit using 600 x 600 x 6 mm GI plate type electrode with top funnel with wire-mesh with all neccessary material and Including supply and erection of pre cast cement concrete 450 mm x 450 mm x 450 mm chamber, watering arrangement, CI cover etc complete as per ISI 3043-1987. (Result required Min. 1 Ohm) | 15 | nos
6 | Providing and making Earthing Pit using 600 x 600 x 3 mm Copper plate type electrode with top funnel with wire-mesh with all neccessary material and Including supply and erection of pre-cast cement concrete 450 mm x 450 mm x 450 mm chamber, watering arrangement, CI cover etc complete as per ISI 3043-1987. (Result required Min. 0.5 Ohm) | 4 | nos
7 | Providing and making Earthing Pit using Pipe in pipe chemical earthing using 50 mm dia outer Copper coated pipe and inner 32 x 10 copper coated strip, 3000 mm long electrode with all neccessary filling material high conductive and anti corossive crystaline conductive mixture atleast 50 kgs and Including supply and erection of pre-cast cement concrete 450 mm x 450 mm x 450 mm chamber, CI cover etc complete as per ISI 3043-1987. (Result required Min. 0.5 Ohm) - | 2 | nos
8 | Providing and laying of following Hot deep G.I. Earth strip for earthing with all required jointing / cutting / welding complete with all hardwares and all welded joints to be painted with black bitumin paints and to be wraped with jute complete to the satisfaction of E.I.C
8a | 32 x 5 mm GI earthing strip | 300 | mts
8b | 25 x 3 mm GI. earthing strip | 50 | mts
8c | 25 x 3 mm Cu. earthing strip | 50 | mts
8d | 8 SWG GI wire | 1200 | mts
8e | 8 SWG Cu. Wire with 20 mm dia. PVC rigid Conduit | 100 | mts
TOTAL - E - EARTHING SYSTEM :
F | INTERNAL WIRING
NOTE : ALL JARIES OR CHASES IN WALLS / COLUMNS / SLABS SHALL BE MADE BY MACHINE AND THE ELECTRICAL CONTRACTOR FOR INSTALLATION OF CONDUITS/ S.B. / BOXES ETC. THE FILLING OF THE SAME IS IN THE SCOPE OF THE ELECTRICAL CONTRACTOR INCLUDING ALL NECCESSARY MATERIAL AND LABOUR COMPLETE. THE RATE SHOULD BE QUOTED ACCORDINGLY.
THE SCOPE OF CONTRACTOR INCLUDES PACKING / UNPACKING / SHIFTING / LOADING / UN-LOADING OF ALL CLIENT SUPPLLIED MATERIALS.
9 | Providing and making point wiring in surface / concealed in slab, walls, furnitures and for above false ceiling, or on ceiling, on beams shall be fixed with saddles and spacers etc., with conduits taken in/on slab with 20 mm dia., 2mm thcik PVC rigid FIA approved ISI marked conduits with bends, tees, elbows, junction boxes etc., with 650 / 1100 V grade ISI marked PVC insulated copper conductor wires i.e. 2 Nos. of 1.5 sq.mm and 1 no of 1.0 sq.mm multi-stranded flexible type single PVC insulated copper conductor wires all accessories screws and washers, modular series switches with all accessories of M.K. India make wraparound / MDS Legrand / ABB make such as 5 amp, 5 pin, socket, one or two way switch all mounted on modular cover plate with flush company made metal box and outlet box of 18 SWG GI with its accessories, angle holder / batten holder / ceiling rose, 3 mm thick hylam cover plates for outlet box etc., electrical point to be complete in all respect to the satisfaction of E.I.C.
a) One 5A switch controlling primary light point
| i) Short Point (Upto 6 Mts) | 250 | pts.
| ii) Medium Point (6.1 Mts to 9 Mts) | 115 | pts.
| iii) Medium Point (9.1 Mts to 12 Mts) | 125 | pts.
| b) Secondary light point looped from nearest primary light point | 1000 | pts.
| c) Two way controlling light point | 30 | pts.
| d) One 5A switch controlling one fan point with fan hook using double fastner fan hook and step control humfree Fan Regulator complete | 625 | pts
| e) 5A socket outlet (5 pin) with 5A SP switch (on common board). | 225 | pts
| f) 5A socket outlet (5 pin) with 5A SP switch (as an independent point) . | 30 | pts
| g) Call bell point with bell push switch | 5 | pts
10 | Supply and installation of 5/15A ( 6 pin) switch socket of M.K. India make Wraparound series / MDS Legrand / ABB make with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Without wiring) | 60 | nos
11 | Supply and installation of 1 no. of 5/15A, 6 pin socket with 1 no. of 15 A switch Plus 1 no. of 5A, 5 pin socket with switch all of M. K. India make Wraparound series / MDS Legrand / ABB make to be on one board with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Without wiring) | 55 | nos
12 | Supply and installation of 1 no. of 5A, 5 pin socket with switch all of M. K. India make Wraparound series / MDS Legrand / ABB make to be on one board with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Without wiring) | 20 | nos
13 | Supply and installation of 2 nos. of 5A, 6 pin sockets and 1 no. of 5/15 A socket with 1 no. of 15 A switch with indicating type all of M. K. India make Wraparound series / MDS Legrand / ABB make to be on one board with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Computer Power supply points) | 240 | nos
14 | Supply and installing 32 A, 230V, Industrial poycarbonate socket outlet with top all enclosed in pre-fabricated powder coated box company made complete duly concealed with all necessary terminations complete to the satisfaction of EIC (For AC). (Without wiring) | 40 | nos
15 | Supply and installation of 32A DP switch of M.K. India make Wraparound series / MDS Legrand / LK pace English model make with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (for AC On/Off and Master Switch) | 70 | nos
16 | Providng, installing, testing, commissioning of mains / sub- mains of following sizes PVC insulated copper conductor multi-stranded flexible type wires with 20 / 25mm dia., 1.5 mm thick FIA approved ISI marked PVC conduits with all accessoreis complete with following wires.
| a) 2 nos. of 2.5 sq mm wires and 1 no. of 1.0 sq mm PVC Insulated copper conductor wires (DB TO SB & SB TO SB & Computer Power Supply). | 8700 | rmt
| b) 2 nos. of 4.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires (15 A / Split AC power plugs). | 3500 | rmt
| c) 4 nos. of 4.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 200 | rmt
| d) 4 nos. of 6.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 250 | rmt
17 | Providng, installing, testing, commissioning of mains / sub- mains of 2 x 2.5 sq.mm and 1 x 1.0 sq.mm PVC insulated copper conductor multi-stranded flexible type FRLS wires in existing conduits / trunking / raceways. Including ferrule numbering to identify the wires in each piece of wire at both the ends etc. complete to the satisfaction of EIC | 1500 | rmt
TOTAL - F - FOR INTERNAL WIRING
G | LIGHTING FIXTURES
18 | Supply ,Installation, testing and commissioning of following Light fixtures etc. Including supply and installation of flexible cords, ball sockets, down rods, hardwares etc. Excluding supply and fabrication of structural steel supports for industrial fixtures in plant bldgs. but inclusive of erection of fixtures with all necessary structural steel supports and to be welded or nut-bolting with all necessary fabrication and drilling etc.complete. (Structural steel supports shall measured and paid extra as per the item in this tender)
18a | 70 W, 7200 Lumens LED Mid Bay fixture with output with necessary assmbly lamp, drivers etc. (PHILIPS MAKE CAT NO. BY400 LED 72S - 7200 Lumens) | 3 | nos.
18b | 19 W, 2000 Lumens LED 1200 mm long light fixture suspending mounted with suspending accessories complete with in-built driver etc complete. (PHILIPS MAKE CAT. NO. Endura LED BN308C LED 20 S) | 1100 | nos.
18c | 19 W, 2000 Lumens LED 1200 mm long light fixture directly mounted on ceiling or wall complete with in-built driver etc complete. (PHILIPS MAKE CAT. NO. Smart Bright BN021C LED 20 S) | 100 | nos.
18d | 10 W, 1000 Lumens LED 600 mm long light fixture directly mounted on ceiling or wall complete with in-built driver etc complete. (PHILIPS MAKE CAT. NO. Smart Bright BN021C LED 10 S) | 10 | nos.
18e | Recessed false ceiling mounted LED FullGlow 600 x 600 mm panel fixture with necessay assembly lamp, drivers, diffusers etc complete (PHILIPS MAKE CAT NO. RC380B LED 30 - 6500, 3000 LUMEN) | 46 | nos.
18f | Recessed false ceiling mounted 1200 Lumens LED downlight fixture with necessay assembly lamp, drivers, diffuser etc complete (PHILIPS MAKE CAT NO. DN172B LED12S -1200 LUMEN) | 10 | nos.
18g | Recessed false ceiling mounted 600 Lumens LED downlight fixture with necessay assembly lamp, drivers, diffuser etc complete PHILIPS MAKE CAT NO. DN171B-LED6S 600 LUMEN) | 10 | nos.
18h | Surface ceiling mounted 1000 Lumens LED fixture with necessay assembly lamp, drivers, etc complete (PHILIPS MAKE CAT NO. SM250 LED 10S-1000 Lumens) | 180 | nos.
19 | Supply, installation, testing and commissioning of PIR sensor suitable of 10 A rated single circuit with day light adjustable, time delay adjustable complete mounted surface / recessed with PVC mounting box complete to the satisfaction of EIC (MK - Honeywell make) | 20 | nos.
20 | Supply, installation, testing and commissioning of PIR sensor suitable of 10 A rated Dual circuit with day light adjustable, time delay adjustable with second circuit suitable for ceiling fan complete mounted surface / recessed with PVC mounting box complete to the satisfaction of EIC (MK - Honeywell make) | 10 | nos.
TOTAL - G - LIGHTING FIXTURES
H | FANS / WALL FANS / EXHAUST FANS
21 | Supply, instalation, testing and commissioning of following Fans / Exhaust fans / Wall fans / Air circulator fans etc.
21a | Ceiling Fan with condensor A.C. 230V. 50 Cys. 900 to1200 mm sweep complete having 3 blades alluminium body and blade sets without regulator, canopy with necesary down rod upto 1000 mm long erected with 3 core 1.5 qs.mm flexible cable with earthing. (Bajaj / Crompton / Havell's) | 625 | nos.
21b | 410 mm sweep, 230V, Ocsillation type, wall mounted decorative fan in-built regulator, tilting facility, hardwares etc. complete (Bajaj / Crompton / Havell's) | 4 | nos.
21c | 300 mm dia. Exhaust fan heavy duty with louvers with all required hardwares complete (Bajaj / Crompton / Havell's) | 17 | nos.
TOTAL - H - FANS / WALL FANS / EXHAUST FANS
I | STREET / AREA LIGHTINGS
22 | Supply, installation, testing and commissioning of Galvanized 6 mts long Octagonal Street light pole. The pole manufactured from HT steel conforming to grade S535JO and base plate Fe 410 conforming to IS 226 / IS 2062 The pole techincal specificaion as under :
The octagonal pole shall be design to withstand the maximum wind speed as per IS 875 and wind speed of min. 169 kM/Hr to be considered. The top loading area and the weight of fixture to be considered to calculate maximaum deflection of the pole.
Top dia (A/F) : 70 mm
Bottom dia. (A/F) : 130 mm
Sheet Thickness : 3 mm
Pole Shaft : Octagonal section and shall be contineous tapered with single longitudinal welding shall be done by Submerged Arc Welding (SAW) process
Base Plate : 220 x 220 x 12 mm thick, The base plate shall be fillet welded to the pole shaft inside as well as outside. The welding shall be done as per qualified MMAW process approved agency.
Door Opening : Door size shall be 500 mm apprx. At 500 mm above base plate. The door shall be vandal resistance and weather proof, flush with exterior surface with locking arrangement.
"J" Bolt size, legnth and nos. : 20 mm size, 600 mm long x 4 nos. (Streel Grade EN8) with template to be provide for erection foundation
Pitch circle dia (PCO) : 205 mm
Projected Bolt legnth : 100 mm
Bracket arm : Single arm, Arm cap shall be 400 mm long, 48 mm dia., 1500 mm long arm. 3.25 mm thick. Hot deep GI. The bracket arm suitable for installing 150 W SON or LED Street light fixtures
Galvanization : The pole shall be hot deep GI as per IS 2629 / IS2633 / IS 4759 standards with average coating thickness of 70 micron single dipping
Cable entry in Pole : The scope includes supply and erection of 40 mm dia DWC pipes 2 or 3 nos. as per requirement. These DWC pipes shall be embeded in Pole RCC foundation.
| Including supply, installation testing and commissioning of 7400 Lumens, 70 W LED Street light fixture (Philips make Cat. No.BRP 409 LED 074 - 7400 Lumens) 3 x 2.5 sq mm unarmoured flexible PVC sheated PVC insulated copper conductor cable from the the fixture to the marshalling box (inside pole), Including supply and fixing of Elmex stud type terminals suitable for loop-in and loop-out 30 A 3 phase 4 wire cable, 4 Amp SP MCB etc complete complete pole to be erected on existing RCC foundations (RCC foundation shall be done by Client's Civil agency). However the foundation bolts with template shall be provided and necessary co-ordination / manufacturer's detail drawings to be provide by the electrical contactor etc. complete to the satisfaction of the E.I.C. | 15 | nos.
23 | Supply, installation, testing and commissioning of street light bracket bend pipe of 32 mm dia., 1.5 mtr long GI `B' Class to be fixed on structural steel column / RCC column / Wall etc with required isupports with necessary welding, anchor fastners etc. complete with necessary 3 core x 1.5 sq.mm PVC insulated sheathed copper conductor cable from fixture to junction box with water tight juction box with Including supply, installation testing and commissioning of 4000 Lumens, 70 W LED Street light fixture (Philips make Cat. No.BRP 409 LED 040 - 4000 Lumens) with all terminations etc. complete as per drawing complete to the satisfaction of EIC | 11 | nos.
24 | Supply, Installation, testing and commissioning of LED Flood light fixtures IP 66 duly mounted on existing installed street light pole with Flood Light fixture (Philips make Cat. No. BVP 410 LED 170 - 17000 Lumens) with Sutable structural steel bracket duly fabricated from ISMC 50 mm channel with m.s. flat clamp with paint one coat of rex- oxide paint and two coats for alluminum / approved paints etc complete as per requirement and drawings. The flood light shall be fitted on the existing street light pole. Including supply and laying of 3 x 1.5 sq.mm PVC insulated copper flexible cable duly laid inside the street pole from fixture to marshelling box and including supply and erection 4 A SP MCB etc complete as per the requirement | 3 | nos.
25 | Supply, installation, testing and commissioning of Small / short Pole, 3 Mts high, 40 mm dia. ms pipe duly powder coated of approved paint / colour with top reducer suitable to install Post Top Luminair (Including supply and installation of Post top luminair fixture) - Philips make Cat. No. BGP 161 LED 2500 Including supply and installation of outdoor FRP junction box having loopin-loopout 16 sq.mm 8 nos. of terminal strip with 1 no. of 6A SP MCB and 3 core x 1.5 sq.mm PVC insulated sheathed copper conductor flexible cable from fixture to junction box complete with 2 nos. of 32 mm dia DWC pipes for cable entries complete with Civil foundation as per requirement (Including supply of all civil materials) with all terminations etc. complete as per drawing complete to the satisfaction of EIC | 24 | nos.
TOTAL - I - STREET LIGHT POLES :
J | STRUCTURED CABLING (DATA / VOICE / TELEPHONE / CCTV / ACCESS CONTROL / AUDIO - Only Passive Components :-
26 | Supply and laying of 20/25 mm dia. 1.5 mm thick, PVC rigid conduit, ISI mark with all accessories complete to be concealed in wall, flooring etc. complete | 600 | mts
27 | Supply and installation of following size PVC trunking with cover and all accessories such as internal, external joints, coupler, angles, cable retainers, etc. complete of M. K. India make / MDS / Precision Plastic co. make complete to the satisfaction of EIC.
27a | 50 x 50 mm | 250 | mts
28 | Supply and installation of 100 mm x 50 mm PVC trunking (cable management system) with cover and all accessories such as internal, external joints, coupler, angles, cable retainers, cable deviders, etc. complete with all required PVC boxes for installation of switches and accessories complete of M. K. India make / MDS make complete to the satisfaction of EIC. | 40 | mts
29 | Supply and installation of following size, 16 SWG G.I. box with top cover of 16 SWG G.I. covers, hardwares, necessary knock-out all sides suitable for conduit complete
29a | 300 mm x 300 mm x 40 mm | 8 | nos.
29b | 150 mm x 150 mm x 40 mm | 15 | nos.
30 | Supply, drawing, laying, testing and commissioning of telephone point wiring using 2 pair 0.41 telephone wire with 20 mm dia., 1.5 mm thick PVC rigid conduit with all accessories with ferrule numbering at both the ends of each piece of cable complete as per the requirement and satisfaction of EIC. | 3000 | Mts
31 | Supply, laying, testing and commissionig of Telephone Outlet RJ 11, of M.K. India make wraparound / MDS Legrand / ABB make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. complete. Including necessary termination etc complete to the satisfaction of EIC. | 80 | Nos
32 | Supply, installation, testing and commissioning of following Pair Krone make telephone tag block with sheet steel enclosure with locking arrangements complete with all necessary terminations etc complete to the satisfaction of EIC
32a | 10 Pair | 4 | Nos
32b | 50 Pair | 1 | Nos
32c | 100 Pair | 1 | Nos
33 | Supply, laying, installation, testing and commissioning of 3 core x 1.5 sq.mm PVC sheathed PVC insulated copper flexible cable with 20 mm dia. 1.5 mm thick PVC rigid conduits with all accessories complete for Access Control power supply complete to the satisfaction of EIC | 100 | Mts
34 | Supply, laying, installation, testing and commissioning of following Pair of 0.51 mm tinned copper PVC insulated PVC sheathed jelly filled armoured telephone cable to be laid in existing cable trench / pull-through pipes or cleated on wall / RCC with supply and fixing of GI saddles / spaceres including all required hardwares etc complete
34a | 10 Pair | 300 | Mts
35 | Supply, laying, testing and commissionig of TV socket Outlet of M.K. India make wraparound / MDS Legrand / ABB make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. complete. Including necessary termination etc complete to the satisfaction of EIC. | 2 | Nos
36 | Supply, laying, installation, testing and commissioning of following RG 6 TV co-axial copper cable with 20 mm dia. 1.5 mm thick PVC rigid conduits with all accessories complete for Access Control power supply complete to the satisfaction of EIC
36a | RG 6 TV Cable | 100 | Mts
37 | Supply, drawing, laying, testing and commissioning of CAT 6 UTP cable in existing conduit / trunking with all accessories with ferrule numbering at both the ends of each piece of cable complete as per the requirement and satisfaction of EIC. | 6000 | Mts
38 | Supply, drawing, laying, testing and commissioning of CAT 6 UTP cable with 20 mm dia., 1.5 mm thick PVC rigid conduit with all accessories with ferrule numbering at both the ends of each piece of cable complete as per the requirement and satisfaction of EIC. | 6000 | Mts
39 | Supply, laying, testing and commissionig of Single Information Outlet RJ 45, CAT 6 with face plate of D-Link / Systimax make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. with complete. Including necessary termination etc complete to the satisfaction of EIC. | 280 | Nos
40 | Supply, laying, testing and commissionig of Dual Information Outlets RJ 45, CAT 6 with dual outlet face plate of D-Link / Systimax make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. with complete. Including necessary termination etc complete to the satisfaction of EIC. | 10 | Nos
41 | Supply, laying, testing and commissioning of following single legnth HDMI cable with both side HDMI connectors complete of following specification of approved make
- Cable Capable of transferring full high definition 1080p signals
- Supports 4K x 2K resolution HDTVs (maximum compliance resolution: 4096 x 2160P @ 24Hz)
- High speed cable 14.93Gbps (Gigabits per second) / 340MHz transfer rate
- Audio Return Channel, Deep Colour and x.v. Colour support
- 24K Gold Plated locking connectors for superior performance and optimum data transfer
- Clip-on ferrites reduce RFI and EMI noise for a purer signal
- High grade 26AWG Oxygen Free Copper conductors for minimum signal loss
- Individually shielded and fully screened to eliminate RF and EM interference
41a | 5 Mts long | 2 | nos.
41b | 10 Mts long | 2 | nos.
41c | 15 Mts long | 4 | nos.
42 | Supply, laying, testing and commissioning of following single legnth VGA double sheilded (Foil & Breaded) cable with both side VGA connectors complete of approved make
42a | 5 Mts long | 2 | nos.
42b | 10 Mts long | 2 | nos.
42c | 15 Mts long | 4 | nos.
43 | Supply, laying, testing and commissioning of clear transperent twin core 1.5 sq.mm / 40/36 mm specially of speaker wire of polycab make / MX make or approval equivelent make with 20 mm dia. PVC rigid conduit with all accessories complete | 2000 | rmt
44 | Supply, installation, testing and commissioning of 6" dia. speaker with acoustic suitable size wooden box or standard box or false ceiling mount with front decorative grill of approved make with LMT (line matching transformer) etc. complete with all necessary terminations complete to the satisfaction to the EIC (Philips / Boss / Ahuja make) | 80 | nos.
45 | Supply, installation, testing and commissioning of Volume control with front modular cover plate of matching with the existing modular cover plate complete to the satisfaction of EIC | 20 | nos.
TOTAL - J - STRUCTURED CABLING (DATA / VOICE / TELEPHONE / CCTV / ACCESS CONTROL
K | RCC HUME / PVC PIPES
46 | Supply laying of following mm dia. RCC hume pipe duly burried under ground for cable entries complete as per the drawings and specification complete to the satisfaction of E.I.C.
46a | 200 mm dia | 12 | mts
47 | Providing and laying of 100 mm dia., 10 kg/cm2 PVC rigid pipe burried under ground in existing cable trencg with all accessories for OFC / Telephone cable complete to the satisfaction of E.I.C. | 200 | mts
48 | Supply and construction of Masonary Chamber 450 X 450 X 600 deep with CI medium duty cover with frame complete with inside smooth plaster complete with line and level considering FGL / RL etc. | 10 | nos
TOTAL - K - RCC HUME / GI PIPES
L | EXCAVATION AND BACKFILLING :
49 | Excavation and backfilling of cable trench 900 mm deep complete with compacting surplus soil and making a good finish level complete to the satisfaction of E.IC. | 200 | Cu.M
50 | Supply and spreading of fine river sand in existing cable trench minimum 300 mm badding etc. complete to the satisfaction of E.I.C. | 70 | Cu.M
51 | Supply and laying of Bricks on the cables in existing cable trench for cable protection complete to the satisfaction of E.I.C. | 6000 | nos
TOTAL - L - EXCAVATION AND BACKFILLING

## Electrical BOQ Sqft format
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Main & Sub-Panels | Supply, Installation, testing and commissioning of PCC, Main and Sub Panels as per drawing and specifications. Panel should be dust and vermin proof (IP-52). Panel shall be fabricated from 14 /16 SWG CRCA sheet metal duly painted with seven tank process and poweder coated of approved paints. Panel consisting of following. Note : All MCCBs shall be Ics = 100 % Icu and to be adjustables. All MCB shall be 10kA - C-Curve, | PCC, Main and Sub Panels | 0 | Nos | 0 | 0
Main & Sub-Panels | MAIN PANEL- Incomming : 400 A TP MCCB, MPR, 50 KA - 400 A, 440V, TPN, Cu. Busbars, 50kA / 1 Sec. - 25 x 6 mm Cu. Earth Busbars, Load managers with all accessories. indicating lamps, Outgoing Feeders : 200 A TP MCCB,T/M, 35 kA, (1 no.) 125 A TP MCCB,T/M, 35 kA, (1 no.) 100 A TP MCCB,T/M, 35 kA, (1 no.) 40/63 A FP MCB, 10 kA (10 nos.) 16 to 32 A DP MCB, 10 kA (2 nos.) | Main Panel | 1 | Nos | 0 | 0
Main & Sub-Panels | SUB PANEL-1 Incomming : 200 A TP MCCB, T/M, 35 KA, 250 A, 440V, TPN, Cu. Busbars, 25 x 6 mm Cu. Earth Busbars, Load managers with all accessories, indicating lamps, Outgoing Feeders : 63 A TP MCCB,T/M, 25 kA, (2 nos.), 40/63 A FP MCB, 10 kA (12 nos.) | Sub Panel-1 | 1 | Nos | 0 | 0
Main & Sub-Panels | SUB PANEL-2 Incomming : 125 A TP MCCB, T/M, 35 KA, 200 A, 440V, TPN, Cu. Busbars, 25 x 3 mm Cu. Earth Busbars, Load managers with all accessories, indicating lamps, Outgoing Feeders : 40/63 A FP MCB, 10 kA (10 nos.) , 16 to 32 A DP MCB, 10 kA (2 nos.) | Sub Panel-2 | 1 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Lighting, Power & Computer Power Supply Distribution Boards | Supply, installing, loading, un-loading, shifting from store with testing and commissioning of metallic double door type distribution board with following MCBs / ELMCBs / RCCBs / etc. with all necessary connections, remaining blank area shall be covered with blanking (dummy) plates etc. complete. (All DBs shall be installed concealed) | Metallic double door type distribution board | 0 | Nos | 0 | 0
Lighting, Power & Computer Power Supply Distribution Boards | 4-WAY TPN PPI DB : Incoming : 40 A FP MCB, Sub Incoming : 32 A DP RCCB - 100 mA (3 nos), Outgoing : 6 to 32 A SP MCB (6 nos) | 4-WAY TPN PPI DB | 1 | Nos | 0 | 0
Lighting, Power & Computer Power Supply Distribution Boards | 6-WAY TPN PPI DB : Incoming : 63 / 40 A FP MCB, Sub Incoming : 40 A DP RCCB - 100 mA (3 nos), Outgoing : 6 to 32 A SP MCB (12 nos) | 6-WAY TPN PPI DB | 10 | Nos | 0 | 0
Lighting, Power & Computer Power Supply Distribution Boards | 8-WAY TPN PPI DB : Incoming : 63 / 40 A FP MCB, Sub Incoming : 40 A DP RCCB - 100 mA (3 nos), Outgoing : 6 to 32 A SP MCB (18 nos) | 8-WAY TPN PPI DB | 12 | Nos | 0 | 0
Lighting, Power & Computer Power Supply Distribution Boards | 4-WAY VTPN DB : Suitable for Incommer FP MCB and SP/TP MCBs as outgoings, Incoming : 63 / 40 A FP MCB, Outgoing : 10 to 32 A TP MCBs (4 Nos.), 10 to 25 A SP MCBs (2 nos.) | 4-WAY VTPN DB | 1 | Nos | 0 | 0
Lighting, Power & Computer Power Supply Distribution Boards | 8 - Way SPN DB : Incoming : 32 A DP RCBO - 30 mA, Outgoing : 6 to 20 A SP MCB (4 nos.) | 8 - Way SPN DB | 1 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Power & Control Cables | Supply, laying, installation, testing and commissioning of armoured PVC / XLPE insulated alumunium / copper conductor of the following sizes in existing cable trench / pull- through pipes / on cable tray or duly cleated on wall / RCC beam / slab / column / structural steel with GI heavy duty patti spacers and GI saddles with necessary drilling and welding on structural steel etc. including supply and fixing alluminium tag numbers at every two meter etc, complete to the satisfaction of EIC (Verify the actual legnth as per the cable schedule and preparing the drum legnth before procurement) | Armoured PVC /XLPE insulated alumunium/copper conductor | 0 | Rmt | 0 | 0
Power & Control Cables | 3.5x120 sq.mm Alu. A2XFY cable | 3.5x120 sq.mm Alu. A2XFY cable | 230 | Rmt | 0 | 0
Power & Control Cables | 3.5x70 sq.mm Alu. A2XFY cable | 3.5x70 sq.mm Alu. A2XFY cable | 180 | Rmt | 0 | 0
Power & Control Cables | 4x16 sq.mm Alu. A2XFY cable | 4x16 sq.mm Alu. A2XFY cable | 600 | Rmt | 0 | 0
Power & Control Cables | 4x2.5 sq.mm Cu. YWY cable | 4x2.5 sq.mm Cu. YWY cable | 400 | Rmt | 0 | 0
Power & Control Cables | 3x2.5 sq.mm Cu. YWY cable | 3x2.5 sq.mm Cu. YWY cable | 300 | Rmt | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
End Terminations | End termination of following PVC / XLPE insulated armoured cables including supply and fixing of brass heavy duty double compression type cable glands with PVC hoods and crimping type long barrel heavy duty copper / alluminum lugs (as per conductor of cable) suitable for terminations of armoured cables, including making connection / terminations of all leads of cables, including drilling and tapping of equipment for cable entries as required and including all labour and materials complete to the satisfaction of E.I.C | End termination PVC / XLPE insulated armoured cables | 0 | Nos | 0 | 0
End Terminations | 3.5x120 sq.mm Alu. A2XFY cable | 3.5x120 sq.mm Alu. A2XFY cable | 6 | Nos | 0 | 0
End Terminations | 3.5x70 sq.mm Alu. A2XFY cable | 3.5x70 sq.mm Alu. A2XFY cable | 2 | Nos | 0 | 0
End Terminations | 4x16 sq.mm Alu. A2XFY cable | 4x16 sq.mm Alu. A2XFY cable | 36 | Nos | 0 | 0
End Terminations | 3 or 4x2.5 sq.mm Cu. YWY cable | 3 or 4x2.5 sq.mm Cu. YWY cable | 80 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Earthing System | Providing and making Earthing Pit using 600 x 600 x 6 mm GI plate type electrode with top funnel with wire-mesh with all neccessary material and Including supply and erection of pre cast cement concrete 450 mm x 450 mm x 450 mm chamber, watering arrangement, CI cover etc complete as per ISI 3043-1987. (Result required Min. 1 Ohm) | Earthing Pit using 600x600x6 mm GI plate | 15 | Nos | 0 | 0
Earthing System | Providing and making Earthing Pit using 600 x 600 x 3 mm Copper plate type electrode with top funnel with wire-mesh with all neccessary material and Including supply and erection of pre-cast cement concrete 450 mm x 450 mm x 450 mm chamber, watering arrangement, CI cover etc complete as per ISI 3043-1987. (Result required Min. 0.5 Ohm) | Earthing Pit using 600x600x3 mm Copper plate | 4 | Nos | 0 | 0
Earthing System | Providing and making Earthing Pit using Pipe in pipe chemical earthing using 50 mm dia outer Copper coated pipe and inner 32 x 10 copper coated strip, 3000 mm long electrode with all neccessary filling material high conductive and anti corossive crystaline conductive mixture atleast 50 kgs and Including supply and erection of pre-cast cement concrete 450 mm x 450 mm x 450 mm chamber, CI cover etc complete as per ISI 3043-1987. (Result required Min. 0.5 Ohm) - | Earthing Pit using Pipe | 2 | Nos | 0 | 0
Earthing System | Providing and laying of following Hot deep G.I. Earth strip for earthing with all required jointing / cutting / welding complete with all hardwares and all welded joints to be painted with black bitumin paints and to be wraped with jute complete to the satisfaction of E.I.C | Hot deep G.I.Earth strip | 0 | Rmt | 0 | 0
Earthing System | 32 x 5 mm GI earthing strip | 32 x 5 mm GI earthing strip | 300 | Rmt | 0 | 0
Earthing System | 25 x 3 mm GI. earthing strip | 25 x 3 mm GI. earthing strip | 50 | Rmt | 0 | 0
Earthing System | 25 x 3 mm Cu. earthing strip | 25 x 3 mm Cu. earthing strip | 50 | Rmt | 0 | 0
Earthing System | 8 SWG GI wire | 8 SWG GI wire | 1200 | Rmt | 0 | 0
Earthing System | 8 SWG Cu. Wire with 20 mm dia. PVC rigid Conduit | 8 SWG Cu. Wire | 100 | Rmt | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Internal Wiring | Providing and making point wiring in surface / concealed in slab, walls, furnitures and for above false ceiling, or on ceiling, on beams shall be fixed with saddles and spacers etc., with conduits taken in/on slab with 20 mm dia., 2mm thcik PVC rigid FIA approved ISI marked conduits with bends, tees, elbows, junction boxes etc., with 650 / 1100 V grade ISI marked PVC insulated copper conductor wires i.e. 2 Nos. of 1.5 sq.mm and 1 no of 1.0 sq.mm multi-stranded flexible type single PVC insulated copper conductor wires all accessories screws and washers, modular series switches with all accessories of M.K. India make wraparound / MDS Legrand / ABB make such as 5 amp, 5 pin, socket, one or two way switch all mounted on modular cover plate with flush company made metal box and outlet box of 18 SWG GI with its accessories, angle holder / batten holder / ceiling rose, 3 mm thick hylam cover plates for outlet box etc., electrical point to be complete in all respect to the satisfaction of E.I.C. | P & M Point wiring | 0 | Nos | 0 | 0
Internal Wiring | One 5A switch controlling primary light point | One 5A switch controlling primary light point | 0 | Nos | 0 | 0
Internal Wiring | Short Point (Upto 6 Mts) | Short Point (Upto 6 Mts) | 250 | Nos | 0 | 0
Internal Wiring | Medium Point (6.1 Mts to 9 Mts) | Medium Point (6.1 Mts to 9 Mts) | 115 | Nos | 0 | 0
Internal Wiring | Medium Point (9.1 Mts to 12 Mts) | Medium Point (9.1 Mts to 12 Mts) | 125 | Nos | 0 | 0
Internal Wiring | Secondary light point looped from nearest primary light point | Secondary light point | 1000 | Nos | 0 | 0
Internal Wiring | Two way controlling light point | Two way controlling light point | 30 | Nos | 0 | 0
Internal Wiring | One 5A switch controlling one fan point with fan hook using double fastner fan hook and step control humfree Fan Regulator complete | One 5A switch | 625 | Nos | 0 | 0
Internal Wiring | 5A socket outlet (5 pin) with 5A SP switch (on common board). | 5A socket outlet (5 pin) with 5A SP switch (on common board). | 225 | Nos | 0 | 0
Internal Wiring | 5A socket outlet (5 pin) with 5A SP switch (as an independent point) . | 5A socket outlet (5 pin) with 5A SP switch (as an independent point) . | 30 | Nos | 0 | 0
Internal Wiring | Call bell point with bell push switch | Call bell point | 5 | Nos | 0 | 0
Internal Wiring | Supply and installation of 5/15A ( 6 pin) switch socket of M.K. India make Wraparound series / MDS Legrand / ABB make with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Without wiring) | 5/15A ( 6 pin) switch socket | 60 | Nos | 0 | 0
Internal Wiring | Supply and installation of 1 no. of 5/15A, 6 pin socket with 1 no. of 15 A switch Plus 1 no. of 5A, 5 pin socket with switch all of M. K. India make Wraparound series / MDS Legrand / ABB make to be on one board with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Without wiring) | 1 no. of 5/15A, 6 pin socket with 1 no. of 15 A switch Plus 1 no. of 5A, 5 pin socket | 55 | Nos | 0 | 0
Internal Wiring | Supply and installation of 1 no. of 5A, 5 pin socket with switch all of M. K. India make Wraparound series / MDS Legrand / ABB make to be on one board with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Without wiring) | 1 no. of 5A, 5 pin socket | 20 | Nos | 0 | 0
Internal Wiring | Supply and installation of 2 nos. of 5A, 6 pin sockets and 1 no. of 5/15 A socket with 1 no. of 15 A switch with indicating type all of M. K. India make Wraparound series / MDS Legrand / ABB make to be on one board with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (Computer Power supply points) | 2 nos. of 5A, 6 pin sockets and 1 no. of 5/15 A socket with 1 no. of 15 A switch | 240 | Nos | 0 | 0
Internal Wiring | Supply and installing 32 A, 230V, Industrial poycarbonate socket outlet with top all enclosed in pre-fabricated powder coated box company made complete duly concealed with all necessary terminations complete to the satisfaction of EIC (For AC). (Without wiring) | 32 A, 230V, Industrial poycarbonate socket outlet | 40 | Nos | 0 | 0
Internal Wiring | Supply and installation of 32A DP switch of M.K. India make Wraparound series / MDS Legrand / LK pace English model make with flush metal box of company made with modular cover plate complete duly concealed with all necessary terminations complete to the satisfaction of E.I.C. (for AC On/Off and Master Switch) | 32A DP switch | 70 | Nos | 0 | 0
Internal Wiring | Providng, installing, testing, commissioning of mains / sub- mains of following sizes PVC insulated copper conductor multi-stranded flexible type wires with 20 / 25mm dia., 1.5 mm thick FIA approved ISI marked PVC conduits with all accessoreis complete with following wires. | PVC insulated copper conductor | 0 | Nos | 0 | 0
Internal Wiring | a) 2 nos. of 2.5 sq mm wires and 1 no. of 1.0 sq mm PVC Insulated copper conductor wires (DB TO SB & SB TO SB & Computer Power Supply). | 2 nos. of 2.5 sq mm wires and 1 no. of 1.0 sq mm PVC Insulated copper conductor wires | 8700 | Rmt | 0 | 0
Internal Wiring | b) 2 nos. of 4.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires (15 A / Split AC power plugs). | 2 nos. of 4.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 3500 | Rmt | 0 | 0
Internal Wiring | c) 4 nos. of 4.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 4 nos. of 4.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 200 | Rmt | 0 | 0
Internal Wiring | d) 4 nos. of 6.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 4 nos. of 6.0 sq mm wires and 1 no. of 2.5 sq mm PVC Insulated copper conductor wires | 250 | Rmt | 0 | 0
Internal Wiring | Providng, installing, testing, commissioning of mains / sub- mains of 2 x 2.5 sq.mm and 1 x 1.0 sq.mm PVC insulated copper conductor multi-stranded flexible type FRLS wires in existing conduits / trunking / raceways. Including ferrule numbering to identify the wires in each piece of wire at both the ends etc. complete to the satisfaction of EIC | Mains / sub- mains of 2 x 2.5 sq.mm and 1 x 1.0 sq.mm PVC insulated copper conductor | 1500 | Rmt | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Lighting Fixtures | Supply ,Installation, testing and commissioning of following Light fixtures etc. Including supply and installation of flexible cords, ball sockets, down rods, hardwares etc. Excluding supply and fabrication of structural steel supports for industrial fixtures in plant bldgs. but inclusive of erection of fixtures with all necessary structural steel supports and to be welded or nut-bolting with all necessary fabrication and drilling etc.complete. (Structural steel supports shall measured and paid extra as per the item in this tender) | Light fixtures | 0 | Nos | 0 | 0
Lighting Fixtures | 70 W, 7200 Lumens LED Mid Bay fixture with output with necessary assmbly lamp, drivers etc. (PHILIPS MAKE CAT NO. BY400 LED 72S - 7200 Lumens) | 70 W, 7200 Lumens LED Mid Bay fixture | 3 | Nos | 0 | 0
Lighting Fixtures | 19 W, 2000 Lumens LED 1200 mm long light fixture suspending mounted with suspending accessories complete with in-built driver etc complete. (PHILIPS MAKE CAT. NO. Endura LED BN308C LED 20 S) | 19 W, 2000 Lumens LED 1200 mm long light fixture | 1100 | Nos | 0 | 0
Lighting Fixtures | 19 W, 2000 Lumens LED 1200 mm long light fixture directly mounted on ceiling or wall complete with in-built driver etc complete. (PHILIPS MAKE CAT. NO. Smart Bright BN021C LED 20 S) | 19 W, 2000 Lumens LED 1200 mm long light fixture | 100 | Nos | 0 | 0
Lighting Fixtures | 10 W, 1000 Lumens LED 600 mm long light fixture directly mounted on ceiling or wall complete with in-built driver etc complete. (PHILIPS MAKE CAT. NO. Smart Bright BN021C LED 10 S) | 10 W, 1000 Lumens LED 600 mm long light fixture | 10 | Nos | 0 | 0
Lighting Fixtures | Recessed false ceiling mounted LED FullGlow 600 x 600 mm panel fixture with necessay assembly lamp, drivers, diffusers etc complete (PHILIPS MAKE CAT NO. RC380B LED 30 - 6500, 3000 LUMEN) | Recessed false ceiling mounted LED FullGlow 600 x 600 mm panel fixture | 46 | Nos | 0 | 0
Lighting Fixtures | Recessed false ceiling mounted 1200 Lumens LED downlight fixture with necessay assembly lamp, drivers, diffuser etc complete (PHILIPS MAKE CAT NO. DN172B LED12S -1200 LUMEN) | Recessed false ceiling mounted 1200 Lumens LED downlight fixture | 10 | Nos | 0 | 0
Lighting Fixtures | Recessed false ceiling mounted 600 Lumens LED downlight fixture with necessay assembly lamp, drivers, diffuser etc complete PHILIPS MAKE CAT NO. DN171B-LED6S 600 LUMEN) | Recessed false ceiling mounted 600 Lumens LED downlight fixture | 10 | Nos | 0 | 0
Lighting Fixtures | Surface ceiling mounted 1000 Lumens LED fixture with necessay assembly lamp, drivers, etc complete (PHILIPS MAKE CAT NO. SM250 LED 10S-1000 Lumens) | Surface ceiling mounted 1000 Lumens LED fixture | 180 | Nos | 0 | 0
Lighting Fixtures | Supply, installation, testing and commissioning of PIR sensor suitable of 10 A rated single circuit with day light adjustable, time delay adjustable complete mounted surface / recessed with PVC mounting box complete to the satisfaction of EIC (MK - Honeywell make) | PIR sensor suitable of 10 A rated single circuit | 20 | Nos | 0 | 0
Lighting Fixtures | Supply, installation, testing and commissioning of PIR sensor suitable of 10 A rated Dual circuit with day light adjustable, time delay adjustable with second circuit suitable for ceiling fan complete mounted surface / recessed with PVC mounting box complete to the satisfaction of EIC (MK - Honeywell make) | PIR sensor suitable of 10 A rated Dual circuit | 10 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Fans / Wall Fans / Exhaust Fans | Supply, instalation, testing and commissioning of following Fans / Exhaust fans / Wall fans / Air circulator fans etc. | Fans / Exhaust fans / Wall fans / Air circulator fans | 0 | Nos | 0 | 0
Fans / Wall Fans / Exhaust Fans | Ceiling Fan with condensor A.C. 230V. 50 Cys. 900 to1200 mm sweep complete having 3 blades alluminium body and blade sets without regulator, canopy with necesary down rod upto 1000 mm long erected with 3 core 1.5 qs.mm flexible cable with earthing. (Bajaj / Crompton / Havell's) | A.C. 230V. 50 Cys. 900 to1200 mm sweep | 625 | Nos | 0 | 0
Fans / Wall Fans / Exhaust Fans | 410 mm sweep, 230V, Ocsillation type, wall mounted decorative fan in-built regulator, tilting facility, hardwares etc. complete (Bajaj / Crompton / Havell's) | 410mm sweep, 230V, Ocsillation type,wall mounted decorative fan | 4 | Nos | 0 | 0
Fans / Wall Fans / Exhaust Fans | 300 mm dia. Exhaust fan heavy duty with louvers with all required hardwares complete (Bajaj / Crompton / Havell's) | 300 mm dia. Exhaust fan heavy duty with louvers | 17 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Street / Area Lightings | Supply, installation, testing and commissioning of Galvanized 6 mts long Octagonal Street light pole. The pole manufactured from HT steel conforming to grade S535JO and base plate Fe 410 conforming to IS 226 / IS 2062 The pole techincal specificaion as under : | Galvanized 6 mts long Octagonal Street light pole | 0 | Nos | 0 | 0
Street / Area Lightings | The octagonal pole shall be design to withstand the maximum wind speed as per IS 875 and wind speed of min. 169 kM/Hr to be considered. The top loading area and the weight of fixture to be considered to calculate maximaum deflection of the pole. Top dia (A/F) : 70 mm, Bottom dia. (A/F) : 130 mm, Sheet Thickness : 3 mm. Pole Shaft : Octagonal section and shall be contineous tapered with single longitudinal welding shall be done by Submerged Arc Welding (SAW) process. Base Plate : 220 x 220 x 12 mm thick, The base plate shall be fillet welded to the pole shaft inside as well as outside. The welding shall be done as per qualified MMAW process approved agency. Door Opening : Door size shall be 500 mm apprx. At 500 mm above base plate. The door shall be vandal resistance and weather proof, flush with exterior surface with locking arrangement. "J" Bolt size, legnth and nos. : 20 mm size, 600 mm long x 4 nos. (Streel Grade EN8) with template to be provide for erection foundation. Pitch circle dia (PCO) : 205 mm. Projected Bolt legnth : 100 mm. Bracket arm : Single arm, Arm cap shall be 400 mm long, 48 mm dia., 1500 mm long arm. 3.25 mm thick. Hot deep GI. The bracket arm suitable for installing 150 W SON or LED Street light fixtures. Galvanization : The pole shall be hot deep GI as per IS 2629/ IS2633 / IS 4759 standards with average coating thickness of 70 micron single dipping. Cable entry in Pole : The scope includes supply and erection of 40 mm dia DWC pipes 2 or 3 nos. as per requirement. These DWC pipes shall be embeded in Pole RCC foundation. | Octagonal pole | 0 | Nos | 0 | 0
Street / Area Lightings | Including supply, installation testing and commissioning of 7400 Lumens, 70 W LED Street light fixture (Philips make Cat. No.BRP 409 LED 074 - 7400 Lumens) 3 x 2.5 sq mm unarmoured flexible PVC sheated PVC insulated copper conductor cable from the the fixture to the marshalling box (inside pole), Including supply and fixing of Elmex stud type terminals suitable for loop-in and loop-out 30 A 3 phase 4 wire cable, 4 Amp SP MCB etc complete complete pole to be erected on existing RCC foundations (RCC foundation shall be done by Client's Civil agency). However the foundation bolts with template shall be provided and necessary co-ordination / manufacturer's detail drawings to be provide by the electrical contactor etc. complete to the satisfaction of the E.I.C. | 7400 Lumens, 70 W LED Street light fixture | 15 | Nos | 0 | 0
Street / Area Lightings | Supply, installation, testing and commissioning of street light bracket bend pipe of 32 mm dia., 1.5 mtr long GI `B' Class to be fixed on structural steel column / RCC column / Wall etc with required isupports with necessary welding, anchor fastners etc. complete with necessary 3 core x 1.5 sq.mm PVC insulated sheathed copper conductor cable from fixture to junction box with water tight juction box with Including supply, installation testing and commissioning of 4000 Lumens, 70 W LED Street light fixture (Philips make Cat. No.BRP 409 LED 040 - 4000 Lumens) with all terminations etc. complete as per drawing complete to the satisfaction of EIC | street light bracket bend pipe of 32 mm dia | 11 | Nos | 0 | 0
Street / Area Lightings | Supply, Installation, testing and commissioning of LED Flood light fixtures IP 66 duly mounted on existing installed street light pole with Flood Light fixture (Philips make Cat. No. BVP 410 LED 170 - 17000 Lumens) with Sutable structural steel bracket duly fabricated from ISMC 50 mm channel with m.s. flat clamp with paint one coat of rex- oxide paint and two coats for alluminum / approved paints etc complete as per requirement and drawings. The flood light shall be fitted on the existing street light pole. Including supply and laying of 3 x 1.5 sq.mm PVC insulated copper flexible cable duly laid inside the street pole from fixture to marshelling box and including supply and erection 4 A SP MCB etc complete as per the requirement | LED Flood light fixtures | 3 | Nos | 0 | 0
Street / Area Lightings | Supply, installation, testing and commissioning of Small / short Pole, 3 Mts high, 40 mm dia. ms pipe duly powder coated of approved paint / colour with top reducer suitable to install Post Top Luminair (Including supply and installation of Post top luminair fixture) - Philips make Cat. No. BGP 161 LED 2500 Including supply and installation of outdoor FRP junction box having loopin-loopout 16 sq.mm 8 nos. of terminal strip with 1 no. of 6A SP MCB and 3 core x 1.5 sq.mm PVC insulated sheathed copper conductor flexible cable from fixture to junction box complete with 2 nos. of 32 mm dia DWC pipes for cable entries complete with Civil foundation as per requirement (Including supply of all civil materials) with all terminations etc. complete as per drawing complete to the satisfaction of EIC | Small / short Pole, 3 Mts high, 40 mm dia. ms pipe | 24 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply and laying of 20/25 mm dia. 1.5 mm thick, PVC rigid conduit, ISI mark with all accessories complete to be concealed in wall, flooring etc. complete | 20/25 mm dia. 1.5 mm thick | 600 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply and installation of following size PVC trunking with cover and all accessories such as internal, external joints, coupler, angles, cable retainers, etc. complete of M. K. India make / MDS / Precision Plastic co. make complete to the satisfaction of EIC. | PVC trunking with cover | 0 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 50 x 50 mm | PVC trunking with cover 50 x 50 mm | 250 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply and installation of 100 mm x 50 mm PVC trunking (cable management system) with cover and all accessories such as internal, external joints, coupler, angles, cable retainers, cable deviders, etc. complete with all required PVC boxes for installation of switches and accessories complete of M. K. India make / MDS make complete to the satisfaction of EIC. | 100 mm x 50 mm PVC trunking | 40 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply and installation of following size, 16 SWG G.I. box with top cover of 16 SWG G.I. covers, hardwares, necessary knock-out all sides suitable for conduit complete | 16 SWG G.I. box with top cover of 16 SWG | 0 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 300 mm x 300 mm x 40 mm | 300 mm x 300 mm x 40 mm | 8 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 150 mm x 150 mm x 40 mm | 150 mm x 150 mm x 40 mm | 15 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, drawing, laying, testing and commissioning of telephone point wiring using 2 pair 0.41 telephone wire with 20 mm dia., 1.5 mm thick PVC rigid conduit with all accessories with ferrule numbering at both the ends of each piece of cable complete as per the requirement and satisfaction of EIC. | Telephone point wiring | 3000 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissionig of Telephone Outlet RJ 11, of M.K. India make wraparound / MDS Legrand/ ABB make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. complete. Including necessary termination etc complete to the satisfaction of EIC. | Telephone Outlet RJ 11 | 80 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, installation, testing and commissioning of following Pair Krone make telephone tag block with sheet steel enclosure with locking arrangements complete with all necessary terminations etc complete to the satisfaction of EIC | Telephone tag block | 0 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 10 Pair | Telephone tag block 10 Pair | 4 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 50 Pair | Telephone tag block 50 Pair | 1 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 100 Pair | Telephone tag block 100 Pair | 1 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, installation, testing and commissioning of 3 core x 1.5 sq.mm PVC sheathed PVC insulated copper flexible cable with 20 mm dia. 1.5 mm thick PVC rigid conduits with all accessories complete for Access Control power supply complete to the satisfaction of EIC | 3 core x 1.5 sq.mm PVC sheathed | 100 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, installation, testing and commissioning of following Pair of 0.51 mm tinned copper PVC insulated PVC sheathed jelly filled armoured telephone cable to be laid in existing cable trench / pull-through pipes or cleated on wall / RCC with supply and fixing of GI saddles / spaceres including all required hardwares etc complete | Pair of 0.51 mm tinned copper PVC insulated PVC sheathed | 0 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 10 Pair | Pair of 0.51 mm tinned copper PVC insulated PVC sheathed - 10 Pair | 300 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissionig of TV socket Outlet of M.K. India make wraparound / MDS Legrand / ABB make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. complete. Including necessary termination etc complete to the satisfaction of EIC. | TV socket Outlet | 2 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, installation, testing and commissioning of following RG 6 TV co-axial copper cable with 20 mm dia. 1.5 mm thick PVC rigid conduits with all accessories complete for Access Control power supply complete to the satisfaction of EIC | RG 6 TV co-axial copper cable | 0 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | RG 6 TV Cable | RG 6 TV Cable | 100 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, drawing, laying, testing and commissioning of CAT 6 UTP cable in existing conduit / trunking with all accessories with ferrule numbering at both the ends of each piece of cable complete as per the requirement and satisfaction of EIC. | CAT 6 UTP cable in existing conduit / trunking | 6000 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, drawing, laying, testing and commissioning of CAT 6 UTP cable with 20 mm dia., 1.5 mm thick PVC rigid conduit with all accessories with ferrule numbering at both the ends of each piece of cable complete as per the requirement and satisfaction of EIC. | CAT 6 UTP cable with 20 mm dia | 6000 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissionig of Single Information Outlet RJ 45, CAT 6 with face plate of D-Link / Systimax make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. with complete. Including necessary termination etc complete to the satisfaction of EIC. | Single Information Outlet RJ 45, CAT 6 | 280 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissionig of Dual Information Outlets RJ 45, CAT 6 with dual outlet face plate of D-Link / Systimax make complete duly mounted on suitable PVC surface box or to be mounted in concealed metallic box etc. with complete. Including necessary termination etc complete to the satisfaction of EIC. | Dual Information Outlets RJ 45, CAT 6 | 10 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissioning of following single legnth HDMI cable with both side HDMI connectors complete of following specification of approved make Cable Capable of transferring full high definition 1080p signals, Supports 4K x 2K resolution HDTVs (maximum compliance resolution: 4096 x 2160P @ 24Hz), High speed cable 14.93Gbps (Gigabits per second) / 340MHz transfer rate, Audio Return Channel, Deep Colour and x.v. Colour support, 24K Gold Plated locking connectors for superior performance and optimum data transfer, Clip-on ferrites reduce RFI and EMI noise for a purer signal, High grade 26AWG Oxygen Free Copper conductors for minimum signal loss, Individually shielded and fully screened to eliminate RF and EM interference | Single legnth HDMI cable with both side HDMI connectors | 0 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 5 Mts long | 5m long - Single legnth HDMI cable with both side HDMI connectors | 2 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 10 Mts long | 10m long - Single legnth HDMI cable with both side HDMI connectors | 2 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 15 Mts long | 15m long - Single legnth HDMI cable with both side HDMI connectors | 4 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissioning of following single legnth VGA double sheilded (Foil & Breaded) cable with both side VGA connectors complete of approved make | single legnth VGA double sheilded cable | 0 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 5 Mts long | 5m long - single legnth VGA double sheilded cable | 2 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 10 Mts long | 10m long - single legnth VGA double sheilded cable | 2 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | 15 Mts long | 15m long - single legnth VGA double sheilded cable | 4 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, laying, testing and commissioning of clear transperent twin core 1.5 sq.mm / 40/36 mm specially of speaker wire of polycab make / MX make or approval equivelent make with 20 mm dia. PVC rigid conduit with all accessories complete | Clear transperent twin core 1.5 sq.mm/40/36 mm | 2000 | Rmt | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, installation, testing and commissioning of 6" dia. speaker with acoustic suitable size wooden box or standard box or false ceiling mount with front decorative grill of approved make with LMT (line matching transformer) etc. complete with all necessary terminations complete to the satisfaction to the EIC (Philips / Boss / Ahuja make) | 6" dia. speaker with acoustic | 80 | Nos | 0 | 0
Structured Cabling (Data/Voice/Telephone/Cctv/Access Control/Audio | Supply, installation, testing and commissioning of Volume control with front modular cover plate of matching with the existing modular cover plate complete to the satisfaction of EIC | Volume control with front modular cover plate | 20 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Rcc Hume / Pvc Pipes | Supply laying of following mm dia. RCC hume pipe duly burried under ground for cable entries complete as per the drawings and specification complete to the satisfaction of E.I.C. | RCC hume pipe | 0 | Rmt | 0 | 0
Rcc Hume / Pvc Pipes | 200 mm dia | 200 mm dia RCC hume pipe | 12 | Rmt | 0 | 0
Rcc Hume / Pvc Pipes | Providing and laying of 100 mm dia., 10 kg/cm2 PVC rigid pipe burried under ground in existing cable trencg with all accessories for OFC / Telephone cable complete to the satisfaction of E.I.C. | 100 mm dia., 10 kg/cm2 PVC rigid pipe | 200 | Rmt | 0 | 0
Rcc Hume / Pvc Pipes | Supply and construction of Masonary Chamber 450 X 450 X 600 deep with CI medium duty cover with frame complete with inside smooth plaster complete with line and level considering FGL / RL etc. | Masonary Chamber 450 X 450 X 600 deep | 10 | Nos | 0 | 0
Group | LineItem Description | Description | Qty | Unit | Rate | Amount
Excavation And Backfilling | Excavation and backfilling of cable trench 900 mm deep complete with compacting surplus soil and making a good finish level complete to the satisfaction of E.IC. | Excavation and backfilling of cable trench 900mm | 200 | CuM | 0 | 0
Excavation And Backfilling | Supply and spreading of fine river sand in existing cable trench minimum 300 mm badding etc. complete to the satisfaction of E.I.C. | Fine river sand | 70 | CuM | 0 | 0
Excavation And Backfilling | Supply and laying of Bricks on the cables in existing cable trench for cable protection complete to the satisfaction of E.I.C. | Bricks on the cables in existing cable trench | 6000 | Nos | 0 | 0